Chernobyl'

In April 1986, Chernobyl' (Chornobyl' in Ukrainian) was an

obscure city on the Pripiat' River in north-central Ukraine.

Almost incidentally, its name was attached to the V.I. Lenin

Nuclear Power Plant located about twenty-five kilometers

upstream.

On April 26, the city's anonymity vanished forever when,

during a test at 1:21 A.M., the No. 4 reactor exploded and

released thirty to forty times the radioactivity of the atomic

bombs dropped on Hiroshima and Nagasaki.  The world first learned

of history's worst nuclear accident from Sweden, where abnormal

radiation levels were registered at one of its nuclear

facilities.

Ranking as one of the greatest industrial accidents of all

time, the Chernobyl' disaster and its impact on the course of

Soviet events can scarcely be exaggerated.  No one can predict

what will finally be the exact number of human victims.  Thirty-

one lives were lost immediately.  Hundreds of thousands of

Ukrainians, Russians, and Belorussians had to abandon entire

cities and settlements within the thirty-kilometer zone of

extreme contamination.  Estimates vary, but it is likely that

some 3 million people, more than 2 million in Belarus' alone, are

still living in contaminated areas.  The city of Chernobyl' is

still inhabited by almost 10,000 people.  Billions of rubles have

been spent, and billions more will be needed to relocate

communities and decontaminate the rich farmland.

Chernobyl' has become a metaphor not only for the horror of

uncontrolled nuclear power but also for the collapsing Soviet

system and its reflexive secrecy and deception, disregard for the

safety and welfare of workers and their families, and inability

to deliver basic services such as health care and transportation,

especially in crisis situations.  The Chernobyl' catastrophe

derailed what had been an ambitious nuclear power program and

formed a fledgling environmental movement into a potent political

force in Russia as well as a rallying point for achieving

Ukrainian and Belorussian independence in 1991.  Although still

in operation, the Chernobyl' plant is scheduled for total

shutdown in 1993.

40

Not for publication

Secret

21 Feb. 79  05363

Return to the General

Section of the Central

Committee of the CPSU

Central Committee of the CPSU

USSR COMMITTEE OF STATE SECURITY [KGB]

February 21, 1979   No. 346-A

Moscow

Construction Flaws at the Chernobyl Nuclear Power Plant [AES]

According to data in the possession of the KGB of the USSR,

design deviations and violations of construction and assembly

technology are occurring at various places in the construction of

the second generating unit of the Chernobyl AES, and these could

lead to mishaps and accidents.

The structural pillars of the generator room were erected

with a deviation of up to 100 mm from the reference axes, and

horizontal connections between the pillars are absent in places.

Wall panels have been installed with a deviation of up to 150 mm

from the axes.  The placement of roof plates does not conform to

the designer's specifications.  Crane tracks and stopways have

vertical drops of up to 100 mm and in places a slope of up to 8.

Deputy head of the Construction Directorate, Comrade V. T.

Gora, gave instructions for backfilling the foundation in many

places where vertical waterproofing was damaged.  Similar

violations were permitted in other sections with the knowledge of

Comrade V. T. Gora and the head of the construction group,

Comrade IU. L. Matveev.  Damage to the waterproofing can lead to

ground water seepage into the station and radioactive

contamination of the environment.

The leadership of the Directorate is not devoting proper

attention to the foundation, on which the quality of the

construction largely depends.  The cement plant operates

erratically, and its output is of poor quality.  Interruptions

were permitted during the pouring of especially heavy concrete

causing gaps and layering in the foundation.  Access roads to the

Chernobyl AES are in urgent need of repair.

Construction of the third high-voltage transmission line is

behind schedule, which could limit the capacity utilization of

the second unit.

As a result of inadequate monitoring of the condition of

safety equipment, in the first three quarters of 1978, 170

individuals suffered work-related injuries, with the loss of work

time totalling 3,366 worker-days.

The KGB of Ukraine has informed the CPSU Central Committee

of these violations.  This is for your information.

Chairman of the Committee [KGB]       [signed] IU. Andropov

...............................................................

42

Secret

Copy no. 1

USSR MINISTRY OF

POWER AND ELECTRIFICATION

(MINENERGO USSR)               Central Committee CPSU

Kitaiskii pr. 7

Moscow, K-74  103074

Minenergo USSR                          Central Committee

of the CPSU

Moscow K-11  A.T. 112604                  MAR. 16, 79  07738

3-16-79  No. 1381-2c                    Return to General

No. ____  from  ______                       Section of the

Central Committee

Checking the structural condition of the first unit of the

Chernobyl AES.

At the instruction of the USSR Minister of Power and

Electrification, a commission under the chairmanship of Deputy

Minister Comrade F. V. Sapozhnikov was formed to check the

quality of construction and assembly work on the first unit of

the Chernobyl AES.

The commission visited the site on March 5-6, 1979, and

examined the state of the buildings and structures of the first

unit of the Chernobyl AES and the notes on the quality of

construction and assembly work.

The Commission found that violations of construction

technology and design deviations have been documented.

In each specific instance, engineering solutions were

adopted (in the construction, the operation, or by the designers)

to eliminate deviations and make the structures conform to the

specifications of the original design and normative documents.

Some of the measures have been realized; the rest of the

work is being completed according to a rigid timetable set by the

commission.

At the present time the power station is operating

successfully, and there are no hindrances to its further

operation.

Taking into account the specifics of nuclear power stations,

and attaching primary significance to the reliability and safety

of their operations, the USSR Ministry of Power and

Electrification has issued an order to enhance monitoring of

technical standards observance and the quality of construction

and assembly work at all AESs under construction.

A letter of similar content was sent to the Central

Committee of the Communist Party of Ukraine.

Deputy Minister          [signed]  P. P. Falaleev

................................................................

Secret

CENTRAL COMMITTEE OF THE CPSU

Defects in the Construction of the Chernobyl AES

Chairman of the KGB of the USSR, Comrade IU. V. Andropov,

reports about the low quality of construction work on various

sections of the second unit of the Chernobyl AES of the USSR

Ministry of Power and Electrification.

As instructed, Comrade Minister P. S. Neporozhnii has formed

a special commission under the leadership of Deputy Minister

Comrade Sapozhnikov to examine and carefully analyze the facts

cited.  The commission visited the site to conduct a thorough

investigation of design deviations and to inspect the system of

monitoring the quality of construction and assembly work.

It was found that in erecting individual pillars, wall

panels, and crane track stopways, there indeed were instances of

deviation from the reference axes and substandard construction

practices.  Most of these deviations were exposed by the design

inspectorate of the Gidroproekt Institute and a technical site

inspection, and they were documented.

The Chernobyl AES construction directorate along with the

design organization and client have adopted coordinated

engineering solutions ensuring design reliability and

construction quality.  Some of the deviations have been

eliminated, and the rest of the measures are being carried out.

A timetable under the control of the Ministry leadership has been

established to eliminate the noted deficiencies.

The specialists conclude that at present there are no

obstacles to the subsequent operation of the Chernobyl AES, and

the electric power station is operating reliably.

To raise the quality of construction and assembly work and

strengthen control over fire and radiation safety, the Ministry

has published instructions stipulating strict verification of the

quality of work at AES construction sites by Ministry

commissions, enhancing quality inspection laws, training

engineers and technicians, strengthening fire-fighting

procedures, and monitoring observation of safety regulations.

....

The Central Committee of the Communist Party of the Ukraine

has been informed of the measures taken by the ministry.

Head of the Section of Machine Building of the

Central Committee of the CPSU.     [SIGNATURE]    (V. Frolov)

March "23", 1979

Nos. 05363,07738,

60A/II.