PUREDATA   C O N N E C T I O N

APPLICATION NOTE

Revised Date:   05/30/90       Bulletin No.   2207

Original Date:  01/15/90       Document No.   022000070000

Eco No.        NA

Product: PUREDATA Twisted Pair

---------------------------------------------------------------------

TITLE: ARCnet twisted pair wiring considerations

The economy, functionality and flexibility of twisted pair

wiring for ARCnet local area networks cannot be denied.  However,

the selection of this wiring scheme opens the door to a host of

potential difficulties.  With adequate pre-planning for the

installation, these difficulties can be minimized or totally

eliminated.

The wiring scheme and its integrity are one of the most

important factors of a network installation.  It is the intention

of this document to outline the suggested application and some of

the more common pitfalls of twisted pair wiring for ARCnet.

Network wiring schemes are evolving at a rapid pace.  The

institution of twisted pair wiring is best suited for structured

cable environments.

General Cable Rules;

* Wiring closet to work area

* 24 American Wire Gauge. (AWG)

* Solid conductors.

* Unshielded.

* Corresponds to IBM type 3 cable specifications.

* Belden 1155A Plenum Rated

* Belden 1154A Non-plenum

Work area patch cables

* 24 American Wire Gauge. (AWG)

* Solid conductors.

* Unshielded.

* Corresponds to IBM type 3 cable specifications

* Belden 1154A Non-plenum

* Belden 1155A Plenum Rated

Hublink patch cables

* Use ONLY the cable supplied with the HUB.

Recommended cable lengths and hub/card configurations

* 400 feet maximum from hub to hub or hub to card.

* Up to ten (10) active hubs may be cascaded.

* Maximum network length is 4,400 feet.

* In BUS topology, maximum of ten cards on same BUS, with a

minimum intercard distance of six feet.

* The maximum length of BUS segment is 400 feet

Polarity

The maintenance of proper polarity of ARCnet twisted pair wire is

crucial to the success of the installation.  PUREDATA twisted

pair interface product provides signalling on pins 2 and 3 of the

RJ-11 connector.  These pins are wired as pin 2 to pin 2 and pin

3 to pin 3.  The pin to pin connection should not be reversed.

In the event that a BALUN (coax to twisted pair converter) is

used in the circuit, one should be aware that most baluns

actually invert the polarity of the signal wires.  This results

in a pin 2 to pin 3, and a pin 3 to pin 2 situation.  The

resulting reversed polarity will induce the network to fail.

If a balun is used in the network, then, in order to defeat the

reversed polarity, the installer should utilize a patch cable

between the balun and the card/hub that inverts pins 2 and 3.

To identify a straight through patch cable, hold the connectors

side by side, and the wire colors should match from left to

right.  If the cable is reversed, then the colors will be

opposite.

Paired Wire Selection

Bundles of twisted pair wire are assembled with specific pairs

that are properly twisted.  It is the twist to the wire that

provides for signal integrity.

It is not sufficient to simply select two wires arbitrarily from

the bundle for data signalling.  Be sure to select an actual pair

for data transmission.

Generally. the Blue-White pair of wire in the bundle is reserved

for data transmission.  One pair of these wires is identified as

Blue with a White stripe, and the other is identified as White

with a Blue stripe.  For further information, consult Belden Wire

and Cables' "A Comprehensive Cabling Guide to Computer

Environments and LANs" page 54.

In summary, the use of "split pairs" is not supported in the

ARCnet environment.

RJ-11 Connection

This connection is very important in that poor terminations can

result in problems that are extremely difficult to isolate.

It is generally inappropriate to crimp solid conductors into

RJ-11 connectors, since these devices were designed to support

stranded wire.  When crimping conductors into the RJ-11, be sure

to incorporate some of the sheath into the connector to act as a

strain relief.  This will provide for a strong and reliable

connection.

Recommended RJ-11 connectors; AMP # 555042-1

Catalog number 78-515

Modular Interconnect Systems

catalog.

Also, when setting up wire distribution from hubs and

workstations, some form of cable "strain relief" must be

provided.  The RJ-11 connectors are delicate devices, and they

are easily displaced within the socket when undue strain is

imparted on them.

Grounding

The hubs and cable distribution system must be properly

grounded.  More than any other cable, unshielded twisted pair

wire is susceptible to induced noise and interference.  The

availability and use of a proper common ground may reduce some or

all of the problems caused due to the nature of this type of

wire.

Be sure to connect the "ground lug" on every hub to an isolated

or protected ground.

Cable Installation Companies

It is important to examine the track record of the organization

selected to install the network cabling system.  Some cable

companies are much more experienced at local area network data

communications than others.  Some simple questioning of the cable

company representative can shed light on whether or not his

company is suited to provided this service.  Keep in mind that

local area network communications is not the same as telephone

technology.

General Considerations

* Mixing voice and data carriers in the same sheath is not

recommended.

* Do not use "Split pairs" in multi-pair cables.

* Using multiple patch panels and shielded cabling will

shorten your distances.

* If wiring any thing other than straight through,

unshielded Cabling, be sure to test it first.

* If installing into an already cabled site, perform a

detailed "site survey" prior to committing to the

customer.

* Provide adequate strain relief to all connectors on the

network.

* Be sure to observe all distance and configuration

limitations.

* Adequate grounding and consistent polarity must be

observed.

* Electrically noisy environments may not be the best sites

possible for twisted pair installations.

* Only use an inverted patch cable if a Balun is used.

* Be sure to properly terminate each network segment.

* Hublink and card terminators are NOT inter-changeable.

If further information is required, please contact:

PURE DATA TECHNICAL SUPPORT

RICHMOND HILL               DALLAS             EUROPE

(416) 731-6444      (214) 242-2040      44-71-924-3505

FAX  (416) 731-7017  FAX (214) 242-9487  FAX 44-71-585-3103

BBS  (416) 492-5980  BBS (214) 242-3225  BBS 44-71-738-2910