���������������������������������������Ŀ

�                                       �

�  EIS - Economic Insulation Selection  �

�                                       �

�             Version 2.2               �

�                                       �

�        Designed and Created By:       �

�        Michael Richardson, P. E.      �

�                                       �

�        Richardson Engineering         �

�         Laurel, Mississippi           �

�                                       �

�����������������������������������������

USERS MANUAL

EIS - Economic Insulation Selection

Copyright 1990-1992 by Richardson Engineering, All Rights Reserved.

TABLE OF CONTENTS             Page

1. General Information                        2

Welcome To EIS                             2

EIS Software                               2

License Agreement                          2

Disclaimer                                 3

2. Introduction                               3

Minimum System Requirements                3

Program Installation                       3

Contents of this Manual                    4

EIS Software Program Listing               5

On-Disk Manual Copy                        5

What EIS Offers You                        6

Who Can Benefit From EIS                   7

3. EIS Program Descriptions                   7

Getting Started                            7

Main Menu Interface                        7

4. Sizing Optimum Insulation Thicknesses      8

EPI and EEI Main Menu                      8

Menu Selection Sequence                    8

Menu Option Description                    8

Data Entry Description                     10

Interpretation of Results                  12

Program Methodology                        14

Program Assumptions                        16

Error Messages                             16

5. Checking Piping Thermal Heat Losses        17

Using EPILOSS                              17

EPILOSS Description                        17

Running in a Memory Resident Mode          17

Data Entry Description                     17

Program Methodology                        18

Interpretation of Results                  19

Program Assumptions                        19

6. Cost File Database Programs                20

EPIDB and EEIDB General Description        20

Main Menu                                  20

Menu Selection Sequence                    21

Menu Entry Description                     21

Supported Insulation Thicknesses & Layers  24

Error Messages                             25

7. User Support                               25

Problems                                   25

Contacting The Author                      25

8. Sample Problems                            26

EPI Sample Problem

EEI Sample Problem

Page 1

EIS - Economic Insulation Selection

1.0  General Information

Welcome To EIS

EIS, (E)conomic (I)nsulation (S)election is a complete, stand-

alone software package for establishing economic selection of

heat containing thermal insulation systems. The following pages

contain complete step-by-step instructions needed for a

computer analysis of insulation requirements.

Richardson Engineering's EIS will calculate insulation

thickness recommendations to meet most desired applications

and will perform the following:

1. Calculate energy losses for various insulation

thicknesses as well as uninsulated, bare surfaces.

2. Determine surface temperatures and identify those

thicknesses that may be insufficient for personnel

protection.

3. Establish installed and operating costs based on

pertinent financial information.

4. Identify the insulation thickness which provides a

minimum operating cost to the owner.

Software

Five design programs are provided in the EIS software package.

The main sizing programs, EPI (Economic Pipe Insulation) and EEI

(Economic Equipment Insulation) use thermal and financial

information to identify optimum insulation sizing for piping and

equipment systems respectively. EPIDB and EEIDB (EPI and EEI

DataBases) are the cost database programs for each respective sizing

program, and allows the user to customize program cost files for

special circumstances. EPILOSS is a heat loss calculation program

and simplifies the analysis of piping system heat losses.

License Agreement

The EIS program software, including EPI, EEI, EPIDB, EEIDB, and

EPILOSS, are commercial software products of Richardson Engineering

Inc. which retains ownership of these programs. Copies of the EIS

software may be licensed for use under the following conditions: A

licensed user may use this software on any compatible computer,

provided the software is used on only one computer and by only one

user at a time.  Licensed users may make a backup copy of the EIS

software, but any other copying of this software or its documentation

is strictly prohibited except when authorized in writing by

Richardson Engineering Inc.

Distributing, renting, sub-licensing, or leasing this

software or documentation without the express written consent

of Richardson Engineering Inc. is strictly prohibited. No one is

permitted to alter, modify or adapt this software or

documentation, including but not limited to, translating,

decompiling, disassembling, or creating derivative works.

The use of this software constitutes acceptance of this

license agreement.

Page 2

Disclaimer

In no event will Richardson Engineering Inc. be liable for any

damages including lost profits, lost savings or other

incidental or consequential damages arising out of the use or

inability to use this product, even if we have been advised

of the possibility of such damages, or for any claim by any

other party. No warranties are made, express or implied, with

regard to the contents of the program and manual, its

merchantability, or fitness for a particular purpose.

2.0 Introduction

Minimum System Requirements

The following are minimum system requirements to run EIS on

your computer.

- IBM PC/XT, AT, PS-2 or 100% compatible computer.

- MS-DOS 2.1, or later.

- Hard disk drive system or floppy disk drive system (*).

- Minimum 256K RAM memory.

- Color monitor (CGA, EGA, or VGA).

- Standard track printer.

(*) Because of higher access speed and superior storage

capacity, we recommend that EIS be run from a hard disk drive

(any size).

Program Installation

Although you can use EIS from a floppy disk drive system, it

works most efficiently from a hard disk. When you receive the

EIS software, follow the following steps to install the system

on your hard drive.

QUICK AUTO INSTALLATION:

1. Insert the EIS Disk 1 diskette in any floppy disk drive.

2. For hard disk installation, type:

INSTALL  (and press Enter at the DOS prompt)

Then follow the screen instructions.

3. To run EIS design software:

At C:\EIS directory, type MENU (press ENTER) <-- Hard Disk

The user may then select the desired program from the main

menu interface.

At A:\ or B:\, the user must insert the specific floppy disk as

described below. Based on the desired program, type the

following:

type EPI (press ENTER)     <--  Floppy Disk No. 1

type EIS (press ENTER)     <--  Floppy Disk No. 1

type EPIDB (press ENTER)   <--  Floppy Disk No. 2

type EEIDB (press ENTER)   <--  Floppy Disk No. 2

type EPILOSS (press ENTER) <--  Floppy Disk No. 2

Page 3

Program Installation - Cont.

ALTERNATE INSTALLATION:

For hard disk systems:

1. Open a new hard disk directory. (Suggest User Name it

EIS).

2. Copy all EIS files from floppy disk to the new directory.

3. If you are using an existing older version of EIS, erase

these files from the hard disk directory (ignore Item 1)

and complete Item 2.

NOTE: ALL EIS Files Must Be Located in The Same Directory

For Proper Program Operation.

Contents of This Manual

This manual shows you step by step in narrative format how to

use each of EIS's features. The best way to learn EIS would

be to go through the whole text while implementing the same

functions on the computer.

Chapter 1 contains general information as well as various

notices.

Chapter 2 is a brief introduction to the EIS design programs,

what it has to offer to the user, and who can benefit.

Chapter 3 provides a brief explanation of each EIS design programs,

including design purpose, function, and data output. The hard drive

main menu interface is also briefly discussed.

Chapter 4 deals with actual use of the EPI and EEI programs and

interpretation of program results. This section includes main

menu selection, data entry information, interpretation of

output data, and descriptions of program assumptions and

error messages.

Chapter 5 deals with actual use of the EPILOSS program and

program functions. This section includes data entry description,

interpretation of results, program methodology, and program

assumptions.

Chapter 6 deals with actual use of the EPIDB and EEIDB programs

and program features. This section includes main menu selection,

data entry information, data review, and interpretation of

error messages.

Chapter 7 deals with user support information.

Chapter 8 explains EPI and EEI sample problems.

Page 4

EIS Software Program Listing

The following program files should be included with your

EIS software package. These files stored on Disk 1 include:

EPI.EXE - EPI Main Program File.

EPICALS.DAT - EPI Calcium Silicate Cost File.

EPIFIBR.DAT - EPI Fiberglass Cost File.

EPICELG.DAT - EPI Cellular Glass Cost File.

EPIMARK.DAT - EPI Contractor Markup Cost File.

SAMPLE1.EPI - Sample EPI Data File.

EEI.EXE - EEI Main Program File.

EEICALS.DAT - EEI Calcium Silicate Cost File.

EEIFIBR.DAT -EEI Fiberglass Cost File.

EEICELG.DAT - EEI Cellular Glass Cost File.

EEIMARK.DAT - EEI Contractor Markup Cost File.

SAMPLE2.EEI - Sample EEI Data File.

INSTALL.EXE - Hard Drive Installation File.

README.TXT - Updated program information.

MENU.EXE - Main EIS Menu Panel (Hard Drive

Installation Only)

The programs stored on Disk 2 include:

EPIDB.EXE - EPI Cost Database Program File.

EEIDB.EXE - EEI Cost Database Program File.

EPILOSS.EXE - EPILOSS Heat Loss Calculator.

MANUAL.DOC - EPI Documentation File (ASCII Text).

COSTBAK.EXE - Self Extracting Archive File Containing

Backup Copy of Cost Database Files.

On-Disk Manual Copy

An "on-disk" manual is supplied with the EIS software and is

identified by the file name "MANUAL.DOC". This on-disk manual

is in ASCII format. You can print it by using DOS commands

or text processor.

To read the contents of this file copy, insert the EIS Disk 2

diskette in your floppy drive. Close door. At the DOS prompt,

type,

TYPE MANUAL.DOC  (press ENTER)

Page 5

On-Disk Manual Copy

The file will scroll down your screen. To stop scrolling,

press CTRL and NUMLOCK keys simultaneously. Then continue

reading.

To print the contents of this manual file, insert EIS Disk 2

diskette in your floppy drive. Close door. Make sure printer

is ready to print approximately 30 pages. At the DOS prompt,

type:

COPY MANUAL.DOC PRN (press ENTER)

What EIS Offers You

EIS is an easy-to-use software package designed to increase

efficiency and productivity in the optimal selection of thermal

insulation.

Energy cost is now a major item in the operation of any new

or existing mechanical process, power generation plant, or

energy system. That is why the selection of the right

thickness, for the application and energy reduction goals

desired, is an important design step that cannot be

overlooked if the system is expected to attain desirable

investment goals.

Additionally, reinsulation after asbestos abatement work will

necessitate a sophisticated approach to insulation selection

in order to maximize long term project effectiveness.

Unfortunately, determining just the "right" thickness is not

an easy task, but anything less than accurate and complete

computer analysis can reduce the best intentions to a

financial burden. Inflation and the rising costs of energy

are known facts and must be accounted for in any insulation

savings projection. Skimping on insulation or "fast payback"

thickness calculations is false economy.

EIS represents a powerful insulation optimization tool in an

easy to use package. Some benefits to be gained are as

follows:

- A complete, stand-alone system. No other software is

necessary.

- Lightning fast program execution.

- Estimated material and labor cost data are built into

the computer. Data input is simplified.

- Built-in comprehensive on-screen reporting for data

evaluation is provided.

- Instant recap for "what-if" type analysis.

- Supports standard printers.

- Displays pertinent installation and operating cost

data necessary for optimal insulation selection.

- Provides the capability to save program data for

recall and evaluation at future dates.

- Graphical review of results.

And many other advanced features ...

Page 6

Who Can Benefit From EIS

EIS is based on established thermal engineering theory and is

suitable for a wide range of industries, trades, and private

and public organizations ranging in size from one-person

individuals to medium and large size contracting companies,

engineers and architects.

3.0 EIS Program Descriptions

As mentioned previously, the EIS insulation sizing package

includes five main sizing programs along with supplemental files

for cost data, contractor markup, and sample application data.

The user should be familiar with the purpose and function of each

program before evaluating any specific design applications.

Additionally, it is recommended that the user "test-drive" each

EIS program before attempting to design an insulation system.

The sample application data are furnished for this purpose.

Finally, it is important that the user understand the general

program methodology and theory for each program.

Getting Started

The EIS program uses two main insulation sizing programs to

identify optimal insulation thicknesses. The EPI (Economic Pipe

Insulation) program is designed for piping applications where the

process temperature exceeds the ambient temperature. The EEI

(Economic Equipment Insulation) program is designed for equipment

(or flat) insulation sizing, and is very similar in function to the

EPI program. Each program uses thermal data to generate system heat

losses, and financial data to identify capital and operating costs

based on a life-cycle costing approach.  Optimal selection is

established by identifying the minimum annualized cost-to-own.

The EPILOSS (EPI Heat Loss) software is a supplemental program for

the EPI piping insulation program. This program allows the user to

initially evaluate an insulation design solely on thermal heat losses

and surface temperatures. For instance, if personnel burn protection

is the primary design criteria, then this program can be used to

identify necessary thicknesses without the need to enter

financial data.

Both the EPI and EEI sizing programs are sensitive to labor and

material costs required for system installation. The cost data

files that are included with the EIS package are estimated amounts

based on average installation conditions. Since insulation

designs may have special site specific cost requirements, the EIS

package contains database programs to revise the EPI and EEI cost

data files. The EPIDB (EPI DataBase) program allows to user to modify

the EPI cost files. Additionally, the EEIDB (EEI DataBase) program

provides for the revision of the EEI cost files.

Main Menu Interface

If the EIS software is installed on a hard drive, a main menu

interface is available for easy selection of the above programs.

After hard disk installation, type MENU from the EIS default

directory prompt. This menu also provides user assistance

including program descriptions, on-line help, and customer

support information.

Page 7

4.0 Sizing Optimum Insulation Thicknesses

EPI and EEI Main Menu

EPI and EEI use a menu driven user interface which allows

for simple selection of various program features. This interface

also is provided with context-sensitive help windows for user

reference. EPI and EEI are designed for the occasional user, with

simple input screens and user-friendly program option

selection.

A schematic of the main menu is as follows:

������������������[ MAIN MENU ]��������������ͻ

�                                             �

�              1) Enter Data                  �

�              2) Look At Results             �

�              3) Review Assumptions          �

�              4) Print Results               �

�              5) Load Data                   �

�              6) Save Data                   �

�              7) Data Units                  �

�              8) Quit                        �

�                                             �

���������������������������������������������ͼ

From this menu, you can access all of the operations of the

program. By using the cursor keys, move the highlighted line

to the desired activity and press the <ENTER> key to select

that option. Press [F1] for additional help messages.

Menu Selection Sequence

Both programs initially require that Option 1 be selected and

completed prior to Looking At Results (Option 2), Printing

Results (Option 4), and Saving Program Data (Option 6). The

user may enter data or load an existing data file from the

computer (Option 5), if available.

English or Metric units may be selected with the use Option 7.

The user may review program assumptions (Option 3) at any

time. Frequent and careful review of this listing is strongly

recommended since some restrictions apply. Special insulation

installations could possibly invalidate program results.

Interpretation by a qualified professional engineer is

suggested.

Menu Entry Description

ENTER DATA (Option 1)

This selection allows the user to enter parameters concerning

the insulation system. Two data windows for this option. A data

window is simply a screen where you enter data requested by the

program. The first window (Thermal Data Window) provides for the

input of project identification and thermal data. The second window

(Financial Data Window) provides for the input of operating and

financial information required for the optimal thickness selection.

As an aid for error checking, all data entry prompts have allowable

ranges which the program will accept. The user will be warned of a

data entry beyond the allowable range.

Page 8

Menu Entry Description - Cont.

LOOK AT RESULTS (Option 2)

Provides a recap screen to review results from Option 1.

Press the ALT C key combination for a graphical display (bar chart)

of analysis results (English Units only).

REVIEW ASSUMPTIONS (Option 3)

Lists program assumptions for user review.

PRINT RESULTS (Option 4)

Allows user to print results from Option 1 to a standard

track printer for hardcopy review. Please note that the use

of a non-standard printers may have unusual results.

LOAD DATA (Option 5)

Allows user to enter the name of an existing data file in the

default drive. Existing data can be recalled from the disk,

modified, and the solution of the modified data set

calculated. Please note that only data files with an EPI or EEI

extension (i.e. Datafile.EPI) can be properly retrieved and

interpreted. Other files retrieved without this extension

will result in a program error.

If you cannot remember the data file name, press [F2] to

search your default directory. The program automatically

identifies those files with the *.EPI or a *.EEI extension.

Move the cursor to the proper data file and press <Enter>. The

program will place the file name in the load window. Press [F10]

for program file loading. Load and use the SAMPLE1.EPI or the

SAMPLE2.EEI datafile for practice.

SAVE DATA (Option 6)

Provides user with a means of storing input data to a file on

the default disk. The program prompts you for the file name. The

file must be a valid DOS file name, up to eight alpha-numeric

characters, without an three letter extension (the EPI or EEI

extension is automatically appended to each data file).

DATA UNITS (Option 7)

Allows the user to select English or Metric (SI) units. Additional

program status information is displayed for reference.

QUIT (Option 8)

This option terminates program execution and places the user

at the DOS prompt.

Page 9

Data Entry Description

The following information provides detail descriptions of

those data entry items which the user must complete prior to

obtaining a recommended economic thickness. Each program

utilizes Option 1 (Data Entry) for user required information.

This option consists of two data windows: 1) Thermal Data

Window and 2) Financial Data Entry Window. For a more general

description of these windows, refer to the previous section.

The entry items are described by window type and include:

THERMAL DATA WINDOW

Project Name - Complete this information so that you can

identify the project. Space is limited. If the name will not

fit, use an abbreviation.

Run Number - Enter this data so that you can identify the

data set during "what-if" type evaluations. That is, if you

perform multiple analysis under the same project name, then

this identification number may be helpful.

Bare Pipe OD (EPI Only) - This data entry refers to the outside

pipe diameter on which the insulation will be installed. Piping

diameters should be entered in inches. The program allows diameters

between 0.5 and 24 inches (SI Units: 0.0127 to 0.6096 meters).

Surface Temperature - This entry establishes the bare surface

temperature in degrees Fahrenheit. The bare surface temperature is

dependant on process temperatures, wall conductivity and thickness,

and surface resistance to heat transfer. For piping, the user may,

in most cases, assume that the pipe interior temperature equals the

surface temperature. For practical purposes, resistance offered by

standard wall pipe is very small. Equipment surface temperatures

will vary by application. In all cases, the user should evaluate

heat transfer to the surface regions.

The program allows surface temperatures between 40 and 1000 degrees

Fahrenheit (SI Units: 4.4 to 538 Degrees C). Additionally, the

user should be aware that insulation materials are limited

regarding temperature ratings.

Ambient Temperature - The temperature of the surrounding

ambient air in degrees Fahrenheit is allowed between a range

of -20 to 150 degrees Fahrenheit (SI Units: -29 to 66 Degrees C).

Conductivity - The values of thermal conductivity , K, for

specific insulation is available from manufacturers, and it

is suggested that data entry be based on information which

apply to the material and brand name of the insulation to be

used. Thermal conductivity is the number of BTU's (British

Thermal Units) which will pass through one square foot of

homogeneous material in one hour with a one degree Fahrenheit

temperature difference per inch of insulation (k = Btu In/Hr,

Sf, Deg F). The program allows for the entry of thermal

conductivity in the range of 0.2 to 0.9 Btu In/Hr, Sf, Deg F

(SI Units: 0.0288 to 0.130 Watts/Meter - Kelvin).

Press the ALT C key combination to graphically display nominal

thermal conductivity information (English units only).

Page 10

Data Entry Description - Cont.

Insulation Code Number - the program supports CALCIUM

SILICATE, FIBERGLASS, and CELLULAR GLASS insulation and has built

in approximated cost values for material and labor installation.

Enter a digit of one (1) for calcium silicate , a digit of

two (2) for fiberglass, or three (3) for cellular glass.

Future updates will include other insulation types.

After the above information has been entered within the

appropriate ranges, press [F10] to view heat loss information

per insulation thickness. After review, press any key for the

Financial Data Window.

FINANCIAL DATA WINDOW

Fuel Cost - Complete the purchased price of fuel in dollars

per million Btu's. The user can calculate this information

from the type and cost of boiler fuel used (i.e. oil, natural

gas, coal) and the fuel heating value. Typical heating values

of fuel are:

Oil: No. 6: 140,000 - 155,000 Btu/Gallon

No. 4: 138,000 - 152,000 Btu/Gallon

No. 2: 134,000 - 146,000 Btu/Gallon

Gas: Natural Gas: 960 - 1,100 Btu/Cubic Foot

Butane: 3,200 Btu/Cubic Foot

Producer Gas: 150 - 200 Btu/Cubic Foot

Coal (or other solid fuel)

Lignite : 8,000 Btu/Pound

Sub-Bituminous : 8,300 - 13,000 Btu/Pound

Bituminous : 11,000 - 14,000 Btu/Pound

Anthracite : 12,000 - 15,500 Btu/Pound

Wood : 4,800 - 6,300 Btu/Pound

Peat : 7,600 - 10,026 Btu/Pound

Bagasse : 8,300 Btu/Pound

The computer accepts fuel costs in the range of 0.1 to 10

dollars per million Btu's (SI Units: 0.0001 to 0.01 $/MegaJoules).

Annual Fuel Inflation (%) - This is an expectation of annual

fuel price increases. Depending on fuel market conditions, 10

percent could be a good estimate. The program accepts an

inflation rate of 0 to 100 percent.

Interest Rate (%) - this represents the value of money and is

always greater than the inflation rate. This represents the

"opportunity cost" if the installation funding was placed in

the best alternate investment. The program accepts an

interest rate between 0 to 100 per cent.

Operating Schedule - This represents the annual operating

hours of the insulation system. The maximum available annual

operating hours is 8760.

Economic Life of New Insulation - Enter the expected life, in

years, of the new insulation. Typical values are between 10

to 20 years. the program accepts a life in the range of 10 to

30 years.

Page 11

Data Entry Description - Cont.

Average Capital Investment Cost of Heat ($/1000 BTU/HR-English or

$/Kilowatts-Metric) This quantity represents the cost of heat

attributed to the heating plant investment (EPI and EEI amortizes

this value to an annual amount). This item is calculated as follows:

Book Value of the Heat Producing Facility ($)

=   ---------------------------------------------   X 1000

The Average Hourly Energy Production (Btu/Hr)

The average hourly energy production rate can be calculated with

various methods, depending on the available data. However, a

common approach is:

Hourly Fuel Use X Conversion Efficiency X Fuel Heating Value

Boiler Efficiency (%) - Input the thermal energy efficiency

of the boiler plant. Efficiencies vary depending on the

boiler and fuel types; however, typical efficiencies range

from 60 to 80 percent. The program can accept 25 to 95

percent efficiencies.

Installation Labor Rate ($) - Enter the hourly labor rate for

local site conditions. Labor rates can vary considerably

due to geographic regions, installation conditions,  labor

agreements, and other site specific occurrences. Refer to

current estimating manuals, insulation contractors, vendors,

or other appropriate sources for hourly wage information.

Interpretation of Results

The following information depicts sample data and program

output created after the completion of Data Entry (Option 1).

Please note that data is entered in the top half of the

screen and output is displayed in the lower screen half. The

user should press [F10] to obtain output after data entry.

The following screen is the Thermal Data Window (EPI example).

��������������������������������������������������������������������ͻ

�           .............  THERMAL DATA WINDOW   .............       �

�Enter Project Name :                                          sample�

�Enter Run Identification :                                    1�����

�Enter OD of Bare Pipe - Inches :                              4�����

�Enter Pipe Temperature - Degrees F :                          500���

�Enter Ambient Temperature - Degrees F :                       40����

�Enter Ave. Insulation Thermal Conductivity - Btu/Sf-Hr-F-In : 0.45��

�Enter Insulation Code Number :                                     1�

�                         *** PROGRAM OUTPUT ***                     �

�No  Layers  Inches of Insulation  BTU Loss/Hr-Lin Ft  Surface Temp-F�

�   1               1.5                 170                110       �

�   1               2.0                 142                 95       �

�   1               2.5                 124                 85       �

�   1               3.0                 112                 78       �

�   1               3.5                 102                 73       �

�   1               4.0                  95                 69       �

�   1               4.5                  89                 66       �

�   1               5.5                  80                 62       �

�   1               6.0                  76                 60       �

�   2               7.0                  71                 57       �

�        The Bare Pipe BTU Loss per Hr-Lineal Ft of Pipe :  1987     �

����������������������Press Any Key To Continue���������������������ͼ

Page 12

Interpretation of Results - Cont.

Output data on the above window denotes heat loss and outer

insulation surface temperature based on insulation thicknesses.

The number of layers per insulation thickness is shown for

additional reference. A bare surface (non-insulated) heat loss

figure is shown at the bottom of the screen. EPI or EEI warns

the user if an insulation surface temperature exceeds 120

degrees Fahrenheit. A "TOO HOT" warning is displayed and

identifies those thicknesses which represent a potential

burn hazard.

The Financial Data Window (EPI example) is shown below. This

window is second screen completed by the user during Option 1.

This screen is also the final data entry point for the

program which uses the financial information to determine

costs required for an optimal insulation selection.

��������������������������������������������������������������������ͻ

�          .............  FINANCIAL DATA WINDOW   .............      �

�                      ** Data Input Needed Here **                  �

�Enter Fuel Cost - $/ Million Btu :                            3�����

�Enter Annual Inflation, Fuel Cost - % :                       10����

�Enter Annual Interest Rate - % :                              12����

�Enter Operating Schedule - Hours Per Year :                   8760��

�Enter Economic Life of New Insulation - Years :               20����

�Enter Average Capital Investment Cost of Heat  - $/MBtu/Hour :2�����

�Enter Boiler Plant Efficiency - %:                            85����

�Enter Installation Labor Rate - $/Hour :                      25����

�                        *** PROGRAM OUTPUT ***                      �

�Number Of Thickness  Material Labor Total Inst  Heat Loss  Cost To  �

�Layers     Inches      $/Ft   $/Ft Cost $/Ft-Yr $/Ft-Yr  Own $/Ft-Yr�

�  1          1.5         6      6      1.77       12.05     13.82   �

�  1          2.0         9      6      2.21       10.09     12.30   �

�  1          2.5        11      7      2.65        8.81     11.46   �

�  1          3.0        13      7      2.94        7.91     10.85   �

�->1          3.5        16      7      3.53        7.23     10.76<- �

�  1          4.0        20      8      4.12        6.71     10.83   �

�  1          4.5        23      9      4.69        6.29     10.98   �

�  1          5.5        29     10      5.89        5.65     11.54   �

�  1          6.0        33     11      6.51        5.40     11.91   �

�  2          7.0        42     20      9.08        5.00     14.08   �

�����������������������Press Any Key To Continue��������������������ͼ

Output data on the above window denotes financial parameters

(including material/labor costs, total installed cost, and

annual cost to own) based on the insulation thickness. The

number of layers per insulation thickness is shown for

additional reference.

Page 13

Program Methodology  (English Units)

Labor and material costs are based on average subcontractor

installed costs with a 25 percent markup (this can be modified

using the EPIDB or EEIDB database engine).

The annual cost to own and operate is the total cost of the

yearly heat losses plus the annual total installed cost. It

is left to the user to examine the total costs and determine

which is the correct insulation system for his application.

Normally, the lowest total cost system would be the correct

selection and is HIGHLIGHTED IN RED on the monitor screen.

The Total Cost To Own ($/Ft-Yr for EPI or $/SF-Yr for EEI) is:

TOTCOST = LOSSVAL + TIC

The total installed cost is an annualized installed cost

based on the initial investment, project life, and cost of

money. The total installed cost of the insulation is

calculated as follows:

TIC = 1.1 X CRF X (Material Cost + Labor Cost)

The factor 1.1 allows for an annual maintenance of 10 percent

on the insulation. CRF is the capital recovery factor which

converts a single payment to a series of annual streams based

on the number of years specified, N, and the cost of money,

I. CRF is calculated as follows:

CRF = (I X (1+I)^N) / ((1+I)^N - 1)

The annual value of the heat loss (LOSSVAL), in $/Ft-Yr for EPI

or $/SF-Yr for EEI, is calculated as shown:

LOSSVAL = BTUVAL X HEATLOSS X HOURS

where: HOURS is the hours per year of operation.

The EPI program calculates heat lost (HEATLOSS), BTU/Hr-Foot, for

a given piping system as follows:

HEATLOSS = (0.523 X TEMPDIF X R2) / ((R2 X LN(R2/R1)/

COND)+.6)

Where:

COND = thermal conductivity, BTU-In/Hr-Sf-F

TEMPDIF = fluid temp - ambient temp, F

R2, R1 = Outside and inside radius of insulation shell

in inches.

0.6 = the surface resistance (reciprocal of the air film

coefficient), 1/(BTU/Hr-Sf-F)

The EEI program calculates heat lost (HEATLOSS), BTU/Hr-Sq Ft, for

a given equipment system as follows:

HEATLOSS = TEMPDIF  / ((W/COND) + 0.6)

Where:

COND = thermal conductivity, BTU-In/Hr-Sf-F

TEMPDIF = fluid temp - ambient temp, F

W = Insulation Thickness, in inches.

0.6 = the surface resistance (reciprocal of the air film

coefficient), 1/(BTU/Hr-Sf-F)

Page 14

Program Methodology - Cont.

The energy value of the insulation heat losses is determined

as follows:

VALUE OF ONE BTU : The value of 1 BTU lost consists of

*  A fuel component (heat loss)

*  A plant capital cost component

*  A plant operating and maintenance cost component.

The value of the fuel component, $/BTU, of lost heat is

calculated as follows:

COSTHEAT = (AVEFAC X COST OF FUEL) / (BOILER EFFICIENCY)

Where: AVGFAC levelizes the escalating fuel cost based on the

inflation rate, L, cost of money, I, and the number of years.

AVEFAC = CRF X (1- (1+L)^N X (1+I)^(-N)) / (I-L)

The plant capital cost component is determined from the

value of the capital investment heat cost, in $ per thousand BTU/Hr,

which is entered by the user.

COSTPLNT = (CRF * CAPITAL INVESTMENT COST OF HEAT)/(1000 * HOURS)

The plant operating and maintenance cost is assumed to be 10

percent of the fuel cost component. Therefore, the value of

one BTU lost is calculated as follows:

BTUVAL = COSTPLNT + 1.1 X COSTHEAT

The user can review a recap screen by selecting Option 2. A

sample output screen (EPI example) is denoted below and based on the

sample output described above.

�������������������������������������������������������������������ͻ

�            .............  ANALYSIS RESULTS   ............         �

�Enter OD of Bare Pipe - Inches :                               4.0 �

�Enter Pipe Temperature - Degrees F :                           500 �

�Enter Ambient Temperature - Degrees F :                         40 �

�Enter Fuel Cost - $/ Million Btu :                             3.0 �

�Enter Annual Inflation, Fuel Cost - % :                         10 �

�Enter Annual Interest Rate - % :                                12 �

�Enter Operating Schedule - Hours Per Year :                   8760 �

�Enter Economic Life of New Insulation - Years :                 20 �

�Enter Installation Labor Rate - $/Hour :                     25.00 �

�                                                                   �

�Number Of Thickness Material Labor Total Inst  Heat Loss  Cost To  �

�Layers    Inches     $/Ft    $/Ft Cost $/Ft-Yr $/Ft-Yr  Own $/Ft-Yr�

�  1         1.5         6      6     1.77       12.05      13.82   �

�  1         2.0         9      6     2.21       10.09      12.30   �

�  1         2.5        11      7     2.65        8.81      11.46   �

�  1         3.0        13      7     2.94        7.91      10.85   �

�->1         3.5        16      7     3.53        7.23      10.76<- �

�  1         4.0        20      8     4.12        6.71      10.83   �

�  1         4.5        23      9     4.69        6.29      10.98   �

�  1         5.5        29     10     5.89        5.65      11.54   �

�  1         6.0        33     11     6.51        5.40      11.91   �

�  2         7.0        42     20     9.08        5.00      14.08   �

����������������������Press Any Key To Continue��������������������ͼ

Page 15

Program Methodology - Cont.

REFERENCE : ECONOMIC THICKNESS FOR INDUSTRIAL INSULATION,

FAIRMONT PRESS, ATLANTA, GA, 1983.

EPI and EEI Program Assumptions

1) Results Are Not Valid For Cold System or Building Insulation.

2) An Air Film Coefficient of 1.67 Btu/Sf-Hr-F Is Assumed.

3) A Maximum Allowable Outer Surface Temperature of 120 Deg F Is Used.

4) Program Uses A Maximum Insulation Thickness of 9 Inches.

5) Program Uses A Maximum Nominal Pipe Diameter of 24 Inches (EPI Only).

6) Material Costs include Insulation with Aluminum Jacket Covering.

7) Calculated Labor and Material Costs Are Estimates. Values should

be verified.

8) SubContractor Installation Assumed with Average Installation

Complexity.

9) Labor & Material Costs Are For Fiberglass, Calcium Silicate, and

Cellular Glass Only.

10) Heating Plant and Insulation Depreciation Periods are Equal.

Error  Messages

Menu Selection Error - Alerts user to an incorrect menu

selection prior to complete data specification of the

insulation system.

Data Selection Error - Alerts user to potential data input

errors which may possibly produce inaccurate program results.

Selected Data File Is Not EPI or EEI Supported - Alerts user to

a file which was not created by the EPI or EEI program.

Insulation Cost Data File Not Found - Alerts user to the

absence of required insulation cost data files within the

default directory. Copy cost data files (they have the file

extension ".DAT") into the EPI and EEI default directory.

Incomplete Cost Data Files or Unsupported Pipe Size (EPI Only) -

Alerts user that the cost data file is corrupted OR that an

unsupported pipe diameter has been entered. Supported nominal

diameters are:

0.5, 0.75, 1.0, 1.5, 2.0, 3.0, 4.0, 5.0, 6.0, 8.0, 10.0,

12.0, 14.0, 16.0, 18.0, 20.0, and 24.0.

If a supported diameter has been entered, the data file may be

corrupted. Copy backup cost data files into the EIS directory.

Page 16

5.0 Using EPILOSS

EPILOSS Description

EPILOSS is designed to supplement the EPI insulation sizing program.

EPILOSS allows the user to evaluate thermal characteristics of

various piping insulation systems without entering associated

financial data which is required by the more comprehensive EPI

(Economic Pipe Insulation) sizing program. The user can enter pipe

size, insulation conductivity, and system temperatures. The EPILOSS

program will respond with pre-determined insulation thicknesses,

insulated and uninsulated piping heat losses, surface temperatures,

and inappropriate thicknesses which do not provide adequate burn

personnel protection.  Since data entry is much more compact,

insulation type and energy characteristics can be quickly evaluated.

Additionally the user may, as an option, configure the program in

metric units, or load EPILOSS as a memory resident program. Loading

in a memory resident mode allows the user to run other design

programs while retaining EPILOSS in memory. The user can "pop-up"

EPILOSS by pressing a defined keyboard hotkey combination.

Running In a Memory Resident Mode

EPILOSS can be run as a memory resident program. The process of

loading EPILOSS as a memory resident program causes your computer

to exit the EPILOSS program and return you to the DOS command

prompt. You are now ready to run any other programs you choose, but

EPILOSS is still in your computer's memory, ready to be activated

at any time by simultaneously pressing the CTRL - E hotkey

combination.

EPILOSS requires approximately 80K of RAM. Therefore the user

must ensure that memory is available prior to loading EPILOSS.

A check can be made by running DOS's CHKDISK program. Other

requirements include an 80 column visual display in TEXT mode.

EPILOSS will NOT "pop-up" in a graphics mode.

Some memory resident programs may conflict with proper program

function. If this occurs, remove these programs from memory before

running EPILOSS.

Data Entry Description

This following information provides detail descriptions of

those data entry items which the user must complete prior to

obtaining a system heat loss analysis.

Bare Pipe OD - This data entry refers to the outside pipe

diameter on which the insulation will be installed. Piping

diameters should be entered in inches. The program allows

diameters between 1 inch and 24 inches (SI Units: 0.0127 to

0.6096 Meters).

Page 17

Data Entry Description - Cont.

Pipe Temperature - This entry establishes the pipe surface

temperature in degrees Fahrenheit. For practical purposes,

resistance offered by standard wall pipe is very small.

In most cases, the user may assume that the pipe interior

temperature equals the pipe surface temperature. The program

allows surface temperatures between 120 and 1000 degrees

Fahrenheit (SI Units: 4.4 to 538 Degrees C). Additionally, the

user should be aware that insulation materials are limited

regarding temperature ratings.

Ambient Temperature - The temperature of the surrounding

ambient air in degrees Fahrenheit is allowed between a range

of 20 to 120 degrees Fahrenheit (SI Units: -29 to 66 Degrees C).

Conductivity - The values of thermal conductivity , K, for

specific insulation is available from manufacturers, and it

is suggested that data entry be based on information which

apply to the material and brand name of the insulation to be

used.  Thermal conductivity is the number of BTU's (British

Thermal Units) which will pass through one square foot of

homogeneous material in one hour with a one degree Fahrenheit

temperature difference per inch of insulation (k = Btu In/Hr,

Sf, Deg F). The program allows for the entry of thermal

conductivity in the range of 0.1 to 0.9 Btu-In/Hr, Sf, Deg F

(SI Units: 0.0288 to 0.130 Watts/Meter - Kelvin).

A conductivity chart will display nominal design numbers for

the three major piping insulation groups including: 1) Calcium

Silicate; 2) Fiberglass; and 3) Cellular Glass. This chart will

pop-up as the user enters the conductivity data entry field.

Additionally, EPILOSS automatically checks user data entry.

If entered data is invalid, the program will flag the user

of an error and will request that the user re-enter the data.

The user will need to use the keyboard cursor keys to correct

or revise data which has been entered.

It is recommended that the user try several practice problems,

utilizing the necessary keyboard functions, before attempting

any design problems.

Program Methodology  (English Units)

The program calculates the heat lost (HEATLOSS), BTU/Hr-Foot,

for a given piping system as follows:

HEATLOSS = (0.523 X TEMPDIF X R2) / ((R2 X LN(R2/R1)/

COND)+.6)

Where:

COND = thermal conductivity, BTU/Hr-Sf-F-In

TEMPDIF = fluid temp - ambient temp, F

R2, R1 = Outside and inside radius of insulation shell

in inches.

0.6 = the surface resistance (reciprocal of the air film

coefficient), 1/(BTU/Hr-Sf-F)

Unit heat losses per square foot are also calculated and shown.

Page 18

Interpretation of Results

The following information depicts sample data and program

output created after the completion of data entry. The

user should verify data entry before requesting a program

analysis. The following screen depicts sample program output:

���������������������������������������������������������������������ͻ

�              .............  ENTER THERMAL DATA  .............       �

�                                                                     �

� Enter OD of Bare Pipe - Inches :                              4�����

� Enter Pipe Temperature - Degrees F :                          500���

� Enter Ambient Temperature - Degrees F :                       20����

� Enter Ave. Insulation Thermal Conductivity - Btu/Sf-Hr-F-In : 0.45��

�                                                                     �

�                          *** PROGRAM OUTPUT ***                     �

�   Inches of Insulation  BTU/Hr-SF  BTU/Hr-Lin Ft  Surface Temp-F    �

�         1.0               218          228            122 TOO HOT   �

�         1.5               170          177             93           �

�         2.0               142          149             77           �

�         2.5               124          130             67           �

�         3.0               111          116             60           �

�         3.5               102          107             54           �

�         4.0                94           99             50           �

�         4.5                88           93             47           �

�         5.0                84           87             45           �

�         5.5                79           83             42           �

�         6.0                76           80             41           �

�         6.5                73           76             39           �

�         7.0                70           74             38           �

� --------------------------------------------------------------      �

�       The Bare Pipe BTU Loss per Hr-Lineal Ft of Pipe :  2037       �

������������Press C To Continue or Any Other Key To Quit�������������ͼ

Output data denotes heat loss and outer insulation surface

temperature based on insulation thicknesses. A bare pipe (non-

insulated) heat loss figure is shown at the bottom of the

screen.  EPILOSS warns the user if an insulation surface

temperature exceeds 120 degrees Fahrenheit. A "TOO HOT"

warning is displayed and identifies those thicknesses which

represent a potential burn hazard.

EPILOSS Program Assumptions

1) Results Are Not Valid For Cold System, Flat, or Building

Insulation.

2)  An Air Film Coefficient of 1.67 Btu/Sf-Hr-F Is Assumed.

3)  A Maximum Allowable Outer Surface Temperature of 120 Deg F Is

Used.

4)  Program Uses A Maximum Insulation Thickness of 7 Inches.

5)  Program Uses A Maximum Nominal Pipe Diameter of 24 Inches.

6)  Pipe Wall Temperature Assumed Equal To Process Temperature.

Page 19

6.0 Cost File Database Programs

EPIDB and EEIDB Description

EPIDB and EEIDB are stand-alone software programs for generating

customized cost database files for the EPI and EEI insulation

sizing programs. The following pages contain complete step-by-step

instructions needed to fully utilize program capabilities.

Richardson Engineering's EPIDB and EEIDB will create cost files to

meet most desired applications and will perform the following:

1. Permits the user to create cost database files based

on the three major insulation material groups including:

1) Calcium Silicate; 2) Fiberglass; and 3) Cellular

Glass.

2. Allows the user to generate customized cost data files

based on site specific material and installation

requirements.

3. Simplifies data entry and permits the user to easily

review and modify cost data within existing files.

The few simple rules in using EPIDB and EEIDB are:

--The user must define the unit material prices and

unit labor rates before building a cost database.

--Since these costs may vary greatly by geographical

region, installation complexity, and contractor,

the user must carefully verify ALL database cost

information.

Main Menu

EPIDB and EEIDB include a menu driven user interface which

allows for simple selection of various program features. This

interface also is provided with context-sensitive help windows

for user reference. Both programs are designed for the occasional

user, with simple input screens and user-friendly program option

selection.

A schematic of the main menu is as follows:

������������������[ MAIN MENU ]��������������ͻ

�                                             �

�                                             �

�            1) Select Insulation             �

�            2) Look At Database              �

�            3) Enter Cost Data               �

�            4) Enter MarkUp                  �

�            5) Reset Database                �

�            6) Quit Program                  �

�                                             �

�                                             �

���������������������������������������������ͼ

Page 20

Main Menu - Cont.

From this menu, you can access all of the operations of the

program. By using the cursor keys, move the highlighted line

to the desired activity and press the <ENTER> key to select

that option. Press [F4] for additional help messages.

Menu Selection Sequence

When creating a NEW cost database, each program initially requires

that Option 5 be completed. The RESET DATABASE creates the necessary

program files and organizes the data files for new data entry.

Please note that this menu item must be carefully utilized since

existing cost files will be destroyed if the user activates the

file reset feature.

Menu Entry Description

SELECT INSULATION (Option 1)

This selection allows the user to select the insulation database.

Available database material groups are:

1) Calcium Silicate

2) Fiberglass

3) Cellular Glass

This menu item should be selected when you first run either

program.  A selection allows the program to access and "open"

the correct cost data files for user input or review. Subsequent

user operations are dependant on the correct database which is

open. The default selection is Calcium Silicate.

LOOK AT DATABASE (Option 2)

Provides a recap screen to review results from Menu Item 3.

For EPI, the user selects the appropriate pipe size from the

corner selection window and presses [F10] to continue. Pipe

selection is not required for the EEIDB program. Both programs

will access the open insulation data file and display the file's

contents which include pipe size, insulation thickness, unit

material costs (EPI displays dollars per lineal foot of pipe

while EEI displays dollars per square feet of insulation), and

unit labor manhour rates (EPI displays manhours per lineal foot

of pipe while EEI displays manhours per square feet on insulation).

Please note that the cost and labor information should be DIRECT

amounts (i.e. no inclusion of indirect job costs). A separate menu

selection item (Item 4) is provided to account for contractor

markup due to overhead and profit requirements. More discussion of

this will be explained in the ENTER COST DATA menu selection

description.

Page 21

Menu Entry Description - Cont.

The following is an example re-cap screen (EEIDB example) of this

menu selection:

������������������������������������������������������������������ͻ

�             .......... DATABASE REVIEW ..........                �

�                                                                  �

�           Database Opened For :  Calcium Silicate                �

�                                                                  �

�    Thickness-In     PipeDia-In    Labor-MH/LF   Material $/LF    �

�                                                                  �

�       1.0               3.0           0.130         3.3          �

�       1.5               3.0           0.160         4.0          �

�       2.0               3.0           0.160         6.0          �

�       2.5               3.0           0.190         7.3          �

�       3.0               3.0           0.190         8.6          �

�       3.5               3.0           0.200         11.0         �

�       4.0               3.0           0.210         13.3         �

�       4.5               3.0           0.240         15.3         �

�       5.0               3.0           0.260         17.4         �

�       5.5               3.0           0.280         19.6         �

�       6.0               3.0           0.300         22.0         �

�       7.0               3.0           0.530         28.0         �

�       8.0               3.0           0.530         33.3         �

�       9.0               3.0           0.580         38.7         �

�                                                                  �

�                                                                  �

�                      End Of Data Review                          �

������������������Press Any Key To Continue ����������������������ͼ

ENTER COST DATA (Option 3)

EPIDB and EEIDB offer an easy and convenient way to enter data. This

menu selection item is utilized to input new or revised cost data

within an opened database. For EPI, the user selects the appropriate

pipe size and presses [F10] to continue. Next, a data entry

"template" is displayed which denotes program supported insulation

thicknesses, layers, and previously entered cost data if the file

already exists. For EEI, the user does not select pipe sizes, but

enters the data directly.

The user defines the necessary cost structure by entering unit

material costs (dollars per lineal foot for EPI or dollars per

square feet of insulation for EEI), and unit labor manhour

rates (manhours per lineal foot for EPI or manhours per square

feet of insulation for EEI) in a columnar fashion, adjacent to the

appropriate thickness and layer.  The following is an example of

the data entry template (EPIDB example):

Page 22

Menu Entry Description - Cont.

������������������������������������������������������������������ͻ

�                .......... DATA ENTRY ..........                  �

�                                                                  �

�           Database Opened For :  Calcium Silicate                �

�                                                                  �

�               Selected Diameter Is : 3.00                        �

�                                                                  �

�       Layer    Thickness-In   Material $/LF  ManHrs/LF           �

�         1          1.0            3.3�         0.13�             �

�         1          1.5            4���         0.16�             �

�         1          2.0            6���         0.16�             �

�         1          2.5            7.3�         0.19�             �

�         1          3.0            8.6�         0.19�             �

�         1          3.5            11��         0.2��             �

�         1          4.0            13.3         0.21�             �

�         1          4.5            15.3         0.24�             �

�         1          5.0            17.4         0.26�             �

�         1          5.5            19.6         0.28�             �

�         1          6.0            22��         0.3��             �

�         2          7.0            28��         0.53�             �

�         2          8.0            33.3         0.53�             �

�         2          9.0            38.7         0.58�             �

�                Begin Fractional Data With Zeros                  �

�         Use Cursor Keys and Enter Data in Column Fashion         �

�����������������������Press F10 To End Input���������������������ͼ

The user should note that cost data entered should be based on

DIRECT costs to be absorbed by the contractor. These direct, or

bare, costs do not include the contractor's overhead and profit

requirements. The Item 4 menu selection, ENTER MARKUP, allows the

user to input a markup multiplier to account for contractor

indirect costs.

In addition, the user should verify that the entered material and

labor costs numbers agree with the associated insulation

thicknesses and layer quantity.

Material cost information and unit labor rates may be obtained from

a variety of sources. Cost estimating manuals, contractor

quotations, and historical plant cost data are potential sources of

information.

ENTER MARKUP (Option 4)

Allows user to enter contractor markup multiplier.

RESET DATABASE (Option 5)

Creates NEW database files and organizes files for data entry. This

menu selection should only be used to generate NEW data files when

the EPIDB or EEIDB program are first used.

Page 23

Menu Entry Description - Cont.

The user should note that existing files will be destroyed if this

menu selection is activated. If the user desires to create

alternate data files based on revised cost structures, the existing

files should be copied to an archive directory - external to the

EIS default directory. It is suggested that this archive directory

be named to reflect the cost data file basis. For example, data

files based on complex installation could be copied to the sample

archive directory tree: C:\EIS\COSTDATA\

EPIDB generates the following piping insulation cost data files:

EPIMARK.DAT - Contractor Markup Data File

EPICALS.DAT - Calcium Silicate Cost Database

EPIFIBR.DAT - Fiberglass Cost Database

EPICELG.DAT - Cellular Glass Cost Database

EPIDB generates the following equipment insulation cost data files:

EEIMARK.DAT - Contractor Markup Data File

EEICALS.DAT - Calcium Silicate Cost Database

EEIFIBR.DAT - Fiberglass Cost Database

EEICELG.DAT - Cellular Glass Cost Database

QUIT PROGRAM (Option 6)

This option terminates program execution and places the user

at the DOS prompt.

Supported Insulation Thicknesses and Layers

EPIDB supports the following pipe insulation thicknesses and layer

quantities:

Insulation Thickness (Inches)    Associated Layer Quantity

1.0                              1

1.5                              1

2.0                              1

2.5                              1

3.0                              1

3.5                              1

4.0                              1

4.5                              1

5.0                              1

6.0                              1

7.0                              2

8.0                              2

9.0                              2

EEIDB supports the following flat thicknesses and layer quantities:

Insulation Thickness (Inches)    Associated Layer Quantity

1.0                              1

1.5                              1

2.0                              1

2.5                              1

3.0                              1

3.5                              1

4.0                              1

4.5                              1

5.0                              1

6.0                              1

7.0                              1

Page 24

Error  Messages

Data File Error - Alerts user to the need to create database files.

This condition normally occurs when first running EPIDB or EEIDB.

Select menu item 4, RESET DATABASE, to generate new data files. In

some cases, existing files may need to be copied to the EIS default

directory. This error will alert the user to the absence of data

files.

Selected Pipe Diameter Not Supported (EPIDB Only) - Alerts user to an

incorrect pipe diameter entry when reviewing data files or entering

new cost information. EPIDB supports the following nominal pipe

diameters (in inches):

0.5             4.0             14.0

0.75            5.0             16.0

1.0             6.0             18.0

1.5             8.0             20.0

2.0            10.0             24.0

3.0            12.0

7.0 General Information

Problems

The use of EIS software is fully supported by Richardson

Engineering. The author of the product will address problems

directly. See "Contacting The Author" in this section

for more information.

Although comments and recommendations from anyone are

appreciated, Richardson Engineering can only provide

technical support for licensed users of this product.

If you have problems with the EIS software, please read this

manual first to make sure you have a thorough understanding of

how the program works and should be used. Richardson Engineering

has sought to provide an error-free product, but because of the

complexity and length of these programs, some rarely-occurring

bugs may exist. If you think you have found a problem, please

take the time to write or call me and explain the problem.

All licensed users will be informed of any problems and their

solutions. Bug-fixes will be provided to licensed users free

of charge. Upgrades to EIS may require a upgrade fee.

Contacting The Author

The best way to contact the author, Michael Richardson, P.E.,

is by writing a letter or postcard to:

Richardson Engineering

P. O. Box 824

Laurel, MS 39441

Another way to contact the author is to leave a message on

the CIME-ISE, "Computers in Mechanical Engineering -

Information and Software Exchange" BBS at (608) 233-3378, 24

hours/day, up to 9600 baud. CIME-ISE is sponsored by ASME.

The author can also be contacted via CompuServe. The author's

user number is 70272,1731.

Page 25

8.0  Sample Problems

The following sample problem is provided to assist the user

in understanding the EIS data input as well as output

interpretation. Two "on-disk" sample files, called SAMPLE1.EPI

and SAMPLE2.EEI, are included if the user desires to review problem

input.

EPI Sample Problem - High Temperature Steam Pipe

An industrial plant steam turbine installation will have a

1,000 foot long, 10 inch NPS high pressure steam line leading

from a steam generator to the turbine generator building. The

superheated steam conditions are 900 PSIA and 850 Degrees F.

The line will be outdoors, where the average ambient temperature

is 62 Degrees F.

The turbine generator will have a maximum output capacity

of 20 megawatts. Total electric generation per year is

expected to be 160 million kWh, and the steam supply line is

expected to be in service 8,000 hours per year. Total expected

capital investment for the steam plant (boiler, piping, condenser,

etc.) is $30 million dollars. The first year fuel cost will

be $50 per ton of coal, which has a heating value of 12,500

Btu/lb. The plant and steam supply line will have a

depreciation period of 25 years (useful service life). The

boiler efficiency is 88 percent, and it requires 10,500 Btu's

of fuel to produce each kWh of electricity.

The return on investment requirement for the company is 12

percent. Fuel cost is expected to increase at an annual

average annual rate of 7 percent.

The insulation to be used on the pipe is calcium silicate

with no more than two layers, and an 0.016 inch aluminum

jacket. Complexity of installation is average (15 to 20

fittings per 100 feet of pipe). The average unit manhour

charge rate is $25 per manhour and is based on local manpower

availability and job conditions. The average direct cost

price estimate per unit on a 10-inch pipe at the time of

construction is as follows (a markup factor is not included;

however, the EPI program uses a 25 percent markup - unless

modified by the EPIDB cost database engine):

Number       Insulation     Direct        Direct

of Layers    Thickness-In  Labor-MH/LF   Material $/LF

1.0           10.0          0.250         6.7

1.5           10.0          0.276         9.4

2.0           10.0          0.303         12.2

2.5           10.0          0.329         15.0

3.0           10.0          0.356         17.8

3.5           10.0          0.382         20.5

4.0           10.0          0.409         23.3

4.5           10.0          0.435         26.1

5.0           10.0          0.462         28.9

5.5           10.0          0.488         31.6

6.0           10.0          0.515         34.4

7.0           10.0          0.787         46.9

8.0           10.0          0.867         54.3

9.0           10.0          0.947         61.8

Page 26

EPI Sample Problem - Cont.

Manually calculate the cost of heat ($ per million Btu):

Price of Coal ($/ton)

=   ----------------------            X 1 million Btu's

2,000 Lbs/ton X Heating Value (Btu/lb)

=   $2.00/million Btu's

Next, manually calculate the average capital investment

cost of heat:

The expected average annual heat production is:

10,500 Btu/kWh X 160 million kWh/year

= 1680 billion Btu's per year

The capital investment of the heating plant (book value) is:

$30 million dollars

The average capital investment cost of heat is calculated

as follows ($/thousand Btu/Hr):

$30 million dollars

=   -------------------------------------- X 1000 Btu's

( 1680 billion Btu / 8,000 Hours per )

per Year            Year

=  $142.9 per thousand Btu/Hr

Please note that EPI will convert this quantity to an annual

amortized amount.

Now, select the menu option 1 (DATA ENTRY) and enter the

following data:

Project Name :                                    Sample Prob

Run Identification :                                        1

OD of Bare Pipe - Inches :                                 10

Pipe Temperature - Degrees F :                            850

Ambient Temperature - Degrees F :                          62

Ave. Insulation Thermal Conductivity - Btu-In/Sf-Hr-F :  0.52

Insulation Code Number :                                    1

After data entry, press F10 to begin program calculation.

Page 27

EPI Sample Problem - Cont.

The calculated thermal output is:

Layers   Inches of Insulation  BTU Loss/Hr-Lin Ft   Surface Temp-F

1               2.00              562.41               168  TOO HOT

1               3.00              421.03               136  TOO HOT

1               3.50              377.74               126  TOO HOT

1               4.00              344.29               119

1               5.00              295.86               108

1               5.50              277.72               104

1               6.00              262.36               101

2               7.00              237.73                96

2               8.00              218.79                92

2               9.00              203.73                88

--------------------------------------------------------------

The Bare Pipe BTU Loss per Hr-Lineal Ft of Pipe : 14276

The TOO HOT flags denote insulation with surface temperatures

exceeding 120 Degrees F and should be avoided since they represent

a potential personnel burn hazard.

Now, enter the following financial data:

Fuel Cost - $/ Million Btu :                                2

Annual Inflation, Fuel Cost - % :                           7

Annual Interest Rate - % :                                  12

Operating Schedule - Hours Per Year :                       8000

Economic Life of New Insulation - Years :                   25

Average Capital Investment Cost of Heat  - $/MBtu/Hour:     142.9

Boiler Plant Efficiency - % :                               88

Installation Labor Rate - $/Hour :                          25

Press F10 for calculation of financial data. The program output

will display the following information:

Thickness  Material   Labor   Total Inst   Heat Loss   Cost To

Inches      $/Ft     $/Ft   Cost $/Ft-Yr   $/Ft-Yr  Own $/Ft-Yr

2.00        15        9       3.47        29.77      33.24

3.00        22       11       4.68        22.29      26.97

3.50        26       12       5.27        20.00      25.27

4.00        29       13       5.88        18.23      24.11

5.00        36       14       7.09        15.66      22.75

5.50        39       15       7.68        14.70      22.38

-->6.00        43       16       8.29        13.89      22.18<--

7.00        59       25      11.67        12.58      24.25

8.00        68       27      13.32        11.58      24.90

9.00        77       30      14.98        10.78      25.76

Based on a minimum total cost to own, the 6 inch insulation thickness

provides the smallest owning cost.

Page 28

EEI Sample Problem

The plant engineer for a wood products factory is considering

insulating a veneer dryer flash tank that is part of a major

energy expansion. The steam/condensate temperature within the

flash tank is 300 Deg F. The ambient temperature averages 60

Deg F. Because of the relatively thin wall thickness and

negligible surface heat resistances, the tank process

temperature shall be used as the surface temperature.

The boiler plant output averages 100,000 pounds of steam per

hour. The steam temperature is 422 Deg F, and pressure is 300

PSIG. The boiler is in operation 8,400 hours per year. The

plant boiler cost is $10 million dollars, with the cost of

money for the facility being 7 percent. The boiler efficiency

is 65 percent, and the depreciation period for the new plant

equipment is 25 years. The fuel to be used is wood residues

(bark, sawdust, etc.), which costs approximately $18 per

short ton and has a fuel heating value is 6000 btu/Lb. Fuel

price is expected to increase at an annual rate of 6 percent.

The insulation to be used on the tank is fiberglass

with no more than one layer, and an 0.016 inch aluminum

jacket. Complexity of installation is average.  The average

unit manhour charge rate is $25 per manhour and is based on

local manpower availability and job conditions.  The average

direct cost price estimate per unit on a 72 inch diameter

vertical tank at the time of construction is as follows (a

markup factor is not included; however, the EEI program uses

a 25 percent markup -unless modified by the EEIDB cost

database engine):

Number       Insulation       Direct        Direct

of Layers    Thickness-In   Labor-MH/LF   Material $/LF

1            1.0            0.134           1.3

1            1.5            0.142           1.7

1            2.0            0.149           2.1

1            2.5            0.157           2.4

1            3.0            0.164           2.8

1            3.5            0.171           3.2

1            4.0            0.179           3.5

1            4.5            0.187           3.9

1            5.0            0.194           4.3

1            5.5            0.201           4.6

1            6.0            0.209           5.0

1            7.0            0.224           5.7

1            8.0            0.239           6.5

1            9.0            0.254           7.2

Manually calculate the cost of heat ($ per million Btu):

Price of Hog Fuel Oil at $18 per ton

=  --------------------------------------------  X 1 million Btu's

2000 Lbs/ton X  Heating Value of 6000 Btu/Lb.

=   $1.5/million Btu's

Page 29

EEI Sample Problem - Continued

Next, manually calculate the average capital investment

cost of heat:

The expected average annual heat production is:

100,000 Lbs Steam/Hr X 1203 Btu/Lb Steam, where 1203 Btu/Lb

is the steam enthalpy

at 300 PSIG

= 120.3 million Btu's per hour

The capital investment of the heating plant (book value) is:

$10 million dollars

The average capital investment cost of heat is calculated

as follows ($/thousand Btu/Hr):

$10 million dollars

=          ----------------------------   X 1000 Btu's

120.3 million Btu's per hour

=  $83.1 per thousand Btu/Hr

Please note that EEI will convert this quantity to an annual

amortized amount.

Now, select the menu option 1 (DATA ENTRY) and enter the

following data:

Project Name :                                    Sample Prob

Run Identification :                                        2

Pipe Temperature - Degrees F :                            300

Ambient Temperature - Degrees F :                          60

Ave. Insulation Thermal Conductivity - Btu-In/Sf-Hr-F :  0.28

Insulation Code Number :                                    2

After data entry, press F10 to begin program calculation.

The calculated thermal output is:

*** PROGRAM OUTPUT ***

Layers  Inches of Insulation  BTU Loss/Hr-Sq Ft  Surface Temp-F

1            1.00               57.53                95

1            1.50               40.29                84

1            2.00               31.00                79

1            2.50               25.19                75

1            3.00               21.21                73

1            3.50               18.32                71

1            4.00               16.12                70

1            5.00               13.00                68

1            6.00               10.89                67

1            7.00                9.38                66

--------------------------------------------------------------

The Bare Surface BTU Loss per Hr / Sq Feet :   667

Note that all of the above insulation thicknesses produce surface

temperatures which are below the recommended limit of 120 Deg F.

Page 30

EEI Sample Problem - Continued

Now, enter the following financial data:

Fuel Cost - $/ Million Btu :                                1.5

Annual Inflation, Fuel Cost - % :                           6

Annual Interest Rate - % :                                  7

Operating Schedule - Hours Per Year :                       8400

Economic Life of New Insulation - Years :                   25

Average Capital Investment Cost of Heat  - $/MBtu/Hour:     83.1

Boiler Plant Efficiency - % :                               65

Installation Labor Rate - $/Hour :                          25

Press F10 for calculation of financial data. The program output

will display the following information:

*** PROGRAM OUTPUT ***

Thickness  Material   Labor   Total Inst   Heat Loss   Cost To

Inches      $/SF     $/SF   Cost $/SF-Yr   $/SF-Yr  Own $/SF-Yr

1.00         2        4       0.55         2.61       3.16

1.50         2        4       0.62         1.83       2.45

2.00         3        5       0.68         1.41       2.09

2.50         3        5       0.75         1.14       1.89

3.00         4        5       0.82         0.96       1.78

3.50         4        5       0.88         0.83       1.71

4.00         4        6       0.95         0.73       1.68

-->5.00         5        6       1.08         0.59       1.67<--

6.00         6        7       1.21         0.49       1.70

7.00         7        7       1.34         0.43       1.77

Based on a minimum total cost to own, the 5 inch insulation thickness

provides the smallest owning cost.

Page 31

End Of Manual